Facility Planning & Control

# 5.   GUIDELINES FOR MECHANICAL DESIGNERS

The following are instructions for the Designer's Mechanical Engineer's use in preparing Mechanical Designs for State Owned projects:

- Mechanical submittal requirements for the Schematic Design and Design Development Phases can be found in the General Instructions to Designers. Mechanical Design/ Documentation services during the Construction Documents Phase consisting of final working drawings and equipment specifications including but not limited to the following:

  - Mechanical Site Plan shall include water supply location and test information.

  - Plumbing details, including water and sewage riser diagrams for all plumbing fixtures.  Show cleanouts on riser diagrams and on floor plans.

  - Plumbing fixture schedules shall be shown either on the drawings or in the Mechanical Specifications

  - Heating, ventilating and air conditioning plans with double line ductwork shown where required, and CFM requirements at each supply, return and exhaust outlet.

  - HVAC details and equipment schedules shall be provided for all devices and appurtenances.

- FPC prefers to use proprietary specifications above all others, whenever possible.  See Instructions on Standard Forms and Specifications for specifics.

- Provide the simplest systems practical then add detail as the design develops.  Energy efficiency, longevity and ease of use are key objectives.  Designer shall match to the extent practical the systems provided to the abilities of facility staff.

- Provide operational redundancy wherever practical.

- Test and rate chillers in accordance with ARI Std. 550/590 latest edition “Standard for Water-Chilling Packages”.  Installation shall comply with ASHRAE Std. 15 “Safety Code for Mechanical Refrigeration”.  When the type and size of a chiller is determined, contact two major manufacturers to obtain the efficiency of the unit.  In all cases, at least two manufacturers must be able to meet the efficiency listed in the specification.  Chillers shall be ARI certified and bear the ARI label.

- The use of multiple compressors and multiple refrigerant circuits is strongly recommended where practical in order to ensure that users are not left without any cooling when chiller problems occur.

- The choice of refrigerants shall be discussed with the User Agency and FPC early during design.  Refrigerants with a global warming potential (GWP) of 700 or greater are prohibited.

- For domestic heating water applications, light commercial electric water heater compliant are preferred with UL 174 or UL 1453 sized for the application.  Provide compression tank with internal diaphragm.  Gas fired equipment may be considered with permission by FPC.

For heating water applications, provide high efficiency gas fired condensing modular boilers designed and tested in accordance with FM/UL requirements latest edition.  Electrical source generation may be considered with permission by FPC.

- Include in the Mechanical Specifications that the Mechanical Contractors shall submit to the Designer, as soon as feasible after award of the Contract, equipment room layouts at a scale not less than 1/4"=1' showing the layout of the actual equipment to be used.  The Designer shall ensure that all specified models fit in the equipment room(s.)  BIM may be utilized for demonstration of fit.

- Use of any asbestos containing materials is strictly prohibited.

- Minimum size of plumbing vents through the roof shall be 2".

- All HVAC penetrations, equipment, pipe and conduit curbs shall be carefully coordinated with the Mechanical Layout, taking care not to have roof penetrations of any kind or runs of pipes within a minimum of one foot from any edge curb, expansion or control joint. The Designer shall endeavor to consolidate roof vents into as few roof penetrations as possible.

- Roof penetration details, supports for mechanical equipment and other related details occurring on roofs including drains, shall be detailed by the architect and shown on the Architectural Drawings.  The Mechanical Engineer shall coordinate all locations with the Designer and verify that the documents reflect the appropriate details.

- All air handlers and water heaters shall have 16-gauge galvanized steel or stainless steel safety drip pans.  Water collected by these pans shall be piped to a floor drain.

- All air handlers shall have double wall construction with access doors and external lube lines for any internal bearings.  The cooling coil casing and the internal drain pan shall be made of stainless steel or other non-corrosive material.  The drain pan shall have a 2-way slope and be IAQ (ASHRAE) specified.

- For new construction, no air conditioning units, ductwork, or cooling towers will be located on the building roof without the prior written approval of FPC.  For renovation work involving the mechanical system, this equipment should be removed from the roof wherever possible. Minimize roof penetrations.  Open air ground HVAC package units are strongly discouraged.

- Variable refrigerant flow systems are permissible by Facility Planning.  Provide integral package controls with user interface sufficient to perform basic diagnostic and set point changes.

- Indicate walking and work surfaces (Walk Pads) on roofs (to be provided by others) for all rooftop (including Mechanical Equipment) that has to be maintained by the User Agency.  Verify and coordinate detailing with the Designer.

- For the Construction Documents Phase transmittal, all duct work from the air handling units through congested areas such as corridors shall be shown double line and shall be drawn to scale.  Architectural Building cross sections of these areas shall be detailed showing all ductwork, piping, etc. to ensure that conflicts do not occur.

- Underground direct bury chilled and hot water piping and fittings shall be pre-insulated steel unless approved otherwise by FPC.  All joints shall be insulated in a manner approved by the piping manufacturer.

- Rooftop chilled and hot water piping and fittings shall be insulated and metal or PVC jacketed unless approved otherwise by FPC.  Supports for all rooftop piping shall be a specified product consisting of steel with rubber foot and set on a corresponding walk pad, not field installed wood supports.  All joints shall be insulated in a manner approved by the piping manufacturer.

- Both Variable Air Volume (VAV) and Direct Digital Control (DDC) systems are required. Pneumatic controls shall not be specified without the approval of FPC.  Existing Pneumatic controls should be replaced   Require vendor to store custom software at the facility site.

- Fume hoods may be equipped with Variable Air Volume (VAV) exhaust and make-up air systems if appropriate. Provide flow tracking between supply and exhaust air systems. Constant flow and low flow fume hood designs may be considered.  Ceiling diffusers in the vicinity of fume hoods should be avoided. Coordinate the connection of fume hoods and fume hood duct work with the Designer.  Where possible, connect multiple fume hoods to a single exhaust fan plenum in order to reduce the number of required exhaust fans.  If practical multiple fans serving an exhaust header is preferred for reliability and safety considerations.

- All Mechanical components shall be chosen with efficiency in mind.  Variable speed drives shall be specified where practical.

- Enthalpy wheels, energy coils, etc. where provided shall have sufficient building automation monitoring to actively report actual heat transfer in BTU/Hr (tons).

- Consider enhanced control of sound and vibration.

- Duct work systems should be self-balancing to the greatest extent practical.  This is particularly true for low pressure portions of the system.

- Water piping in HVAC systems shall be color coded and shall have directional flow arrows along its entire length in the mechanical equipment room.  All zone valves shall be identified by unique numbers in the field and on the drawings with list provided to the User Agency.

- Where HVAC water piping (heating and cooling) has digitally controlled valves, the use of automatic flow control (limiting) devices is prohibited.

- Multi-zone air handlers shall not be used without the written approval of FPC.

- The Mechanical Engineer shall not specify that a factory test of any mechanical equipment should be performed in their presence or otherwise.  Instead, they shall specify that equipment must meet commonly used national Standards such as those of ARI or CTI.

- Buildings and other locations having a fire protection sprinkler system shall be of an approved piping material as listed in the latest adopted edition of the Code except that non-metallic pipe may not be used.  When steel pipe is used, it shall be schedule 40 through 4” diameter.  At the Designer’s discretion, schedule 10 steel pipe may be used for larger pipe sizes.

- It shall be the responsibility of the Designer to, determine the hazard classification of the sprinkler system and identify the hazard classification in the Construction Documents, have performed a flow test during the Schematic Design phase to determine that the quantity and pressure of the water is sufficient for the sprinkler system (with a mandatory 15 pound cushion), show the location where the fire line enters the building, the location of the fire department connection, the location of the sprinkler heads throughout the building and, where required, the location of the fire pump, dry pipe valves, and fully specify the construction materials required for the sprinkler system.  The sprinkler contractor shall prepare and submit shop drawings to the Designer for their review and approval.  The Designer shall submit the shop drawings bearing their shop drawing review stamp to the Fire Marshal's office after it is determined by the Designer that the design is correct.  Plans shall show all areas protected by sprinklers and alternative forms of suppression as well as areas that need special consideration such as dry pipe areas, anti-freeze areas, pipe routes through unheated attics, etc.

- Rolled groove pipe fittings shall be used in sprinkler systems wherever possible.  The use of flanged pipe is discouraged.

- Schedule 40 galvanized steel pipe with rolled grooved fittings shall be used when possible in all dry or pre-action sprinkler systems in order to limit corrosion.  Both the interior and exterior of the galvanized pipe shall be inspected after the grooving process to check for damage to the galvanizing.  Any damaged areas must be repaired before the pipe is put in place.

- Design of any sprinkler system other than wet pipe shall require written approval from FPC.   Gaseous fire suppression systems may be considered in IT or other specialty areas.

- Where required by the Code, water heaters, both electric and gas, shall have installation approval certificates from the state boiler inspector.

- Use external duct insulation where possible to avoid problems with indoor air quality.  The use of internally lined duct will be allowed in special cases where noise attenuation is necessary and with prior written approval of FPC.   Any internal fibrous liner shall be coated against erosion and contamination.

- Heating, where VAV systems are used, shall be an integral part of the VAV box.  Separate perimeter heating shall not be used in such cases without the approval of FPC.

- Under no circumstances shall a room’s temperature be controlled or influenced by two or more thermostats unless the space is sufficiently large that variable heat gain may occur within the zone

- Economizers are preferred but should not be used unless approved by FPC.  The Designer will be expected to document expected performance and effectiveness before acceptance is granted.

- Heating coils shall be included in all areas of the top floor of every building.  Heating coils shall be used in internal areas on floors other than the top floor at the Designer’s discretion.

- Cooling coils shall not have more than 10 fins per inch so that the coils can be easily cleaned.  A density of 12 fins per inch may be considered under special circumstances with approval of FPC.

- Avoid mixing such diverse areas as offices, labs, conference rooms or classrooms on the same VAV box.  A single VAV box shall not serve more than three (3) offices/or similar areas.

- All non-metallic underground lines shall be equipped with a tracer wire and identification tape at the time of installation.

- The latest version of ASHRAE Standard 62.1 and 62.2 shall be used during design in order to provide acceptable indoor air quality.

- Provide branch damper at each supply register or grille.

- Flexible duct attached to ceiling diffusers shall not be more than 5' long.

- The use of duct board for ductwork is prohibited.

- Cooling towers of stainless steel construction is preferred and shall be specified unless approval of FPC is obtained to do otherwise.  The use of corrosion resistant cooling towers may be considered by the Designer, also with approval of FPC.  Cooling towers of galvanized steel construction is prohibited.  Cooling towers shall be Cooling Tower Institute (CTI) certified and bear that label.  Both cross flow and counter flow type cooling towers will be allowed unless the User Agency provides a reasonable, written objection to the use of one of the two types.

- The Designer shall consider the long term cost and ease of operation of both hot water heating and electric heating before choosing the type of heating to use in a building. Do not select heating water systems above 160 degF.

- General purpose buildings shall be kept under a positive pressure of approximately 0.02" water gauge in order to limit the infiltration of indoor air quality contaminants.

- Coordinate required size of equipment rooms with Designer (from small air handling rooms to main boiler rooms) in order to maintain a minimum allowance of three feet (or more if dictated by equipment) around each major piece of equipment.  This applies to each side that requires maintenance of any type and a minimum of 3 sides for access purposes.  Provide additional space for changing filters, motors, shafts, bearings, pumps, etc.  	Provide sufficient space for cleaning and/or replacing tubes in boilers and chillers, shafts, etc. as per the manufacturer’s recommendations.  Depending on the air handler, verify that sufficient clear floor space is provided to allow for the full extension of air handler coils to allow for cleaning and, if needed, replacement without the need for demolition of building components.

- Designer shall insure on drawing and specifications that all penetrations (i.e.  ductwork, piping etc.) in rated vertical and horizontal partitions are properly protected in accordance with referenced codes to maintain the rating of the partition.

- Floor drains in restrooms, janitor’s closets, etc. shall be equipped with a device to insure that the trap does not dry out.

- Mechanical equipment rooms on exterior walls are preferred by FPC wherever possible.

- The Contractor shall hire a Testing and Balancing firm to perform testing and balancing on each project as a cost of the work.  Specific requirements concerning this matter are in the following section.

- Designer shall contact the local fire department to determine the need for fire hydrants.  If fire hydrants are needed for the protection of the facility, they shall be included in the construction contract with approval of FPC.

- Due to homeland security concerns, consider isolating the air flow (exhaust) in mail rooms, lobbies, waiting rooms, and such to ensure that air from those areas is not distributed to other parts of a building.   Fresh air intakes should be located well above the ground when possible.

- All installed ductwork shall be in a clean, new, first class condition.  The Designer shall specify that the Contractor is responsible for keeping the ductwork clean during construction as required using such methods as sealing all openings except when attaching additional sections.  Specifications shall state that air handling units, ductwork and all associated items shall be cleaned or replaced at no cost to the Owner if allowed to get dirty.  All air systems shall have design filters in place during construction and replaced with permanent filters upon completion of project.

- For all air handling systems 2000 cfm and above, minimum filtration that includes two media banks with the first having a MERV 13 nominal efficiency and the second having a minimum MERV 13 nominal efficiency shall be required.

- Commissioning is required to be performed by Louisiana statute and best practice.  Be sure to provide sufficient requirements for the contractor to understand the required level of participation and coordination with the Commissioning Agency including prefunctional testing check lists, system demonstrations, and corrective actions.  Designer shall review final report and make written recommendations to the Owner.

Facility Planning & Control

Testing and Balancing Requirements

State of Louisiana

- The TAB (Testing and Balancing) contract shall be between the Contractor and the TAB firm.

- All TAB deficiencies shall be corrected when found.  Any deficiencies that are (for whatever reason) not corrected immediately shall be shown in the TAB report and listed on a summary sheet in the front of the TAB report.  The TAB report should be submitted and reviewed by the Mechanical Engineer as part of the process to determine substantial completion.  All items on the summary sheet shall become punch list items with dollar values assigned to them.

- TAB firms must be certified by either the AABC (Associated Air Balance Council) or the NEBB (National Environmental Balancing Bureau), or other Owner approved organization, in order to perform work on state projects.  Falsification of a TAB report will not be allowed and will lead to the reporting of that firm to the respective national certification agency.

- Verification of TAB firm certification may be confirmed by contacting the certification agencies.

- FPC reserves the right to hire a second TAB firm to review the TAB report of the first.  FPC also reserves the right to hire a second TAB firm to check the work of the first TAB firm.

- The following “verification” statement shall be included in the TAB section of the Specifications:

“At the time of final inspection, the TAB agency may be required to recheck, in the presence of the Owner's representative, specific and random selections of data, air quantities, and air motion recorded in the certified report.  Points and areas for recheck shall be selected by the Owner's representative.  Measurements and test procedures shall be the same as approved for the initial work for the certified report. Selections for recheck, specific plus random, shall not exceed 10% of the total number tabulated in the report.”

- Shop drawings must be provided to the TAB firm no later than 30 days after the final, approved shop drawings have been returned by the Designer to the Contractor.

- Coordination between the TAB firm and the Contractor shall be left strictly to those parties.

- Duct leakage testing shall be the responsibility of the mechanical contractor or his subcontractor.  Require written report.

- Fire and smoke damper testing shall be done by the Contractor and witnessed by the TAB firm.  Require written report.  Include date, location, damper identifier, deficiencies noted, and pass/fail.

- The Designer shall include TAB work that is required for the full extent of project.

- The TAB contract shall require coordination and demonstration to the commissioning authority as needed.